## THONG_TIN
khoa | gia_tri | nguon
nhom | CM | tên nhóm theo tên tệp catalogue đã duyệt
ten_dong_EN | CM SERIES - CLOSE-COUPLED CENTRIFUGAL PUMP (AQUARIS ghi: CLOSE-COUPLED PUMPS · ELETTROPOMPE MONOBLOCCO) | AQUARIS - Bơm trục ngang CM.pdf tr.1; PEROTAC - Bơm trục ngang CM.pdf tr.1; REDPUMP - Bơm trục ngang CM.pdf tr.1
hang_co | AQUARIS,PEROTAC,REDPUMP | các tệp: AQUARIS - Bơm trục ngang CM.pdf; PEROTAC - Bơm trục ngang CM.pdf; REDPUMP - Bơm trục ngang CM.pdf
tan_so | 50 Hz | AQUARIS - Bơm trục ngang CM.pdf tr.1; PEROTAC - Bơm trục ngang CM.pdf tr.1; REDPUMP - Bơm trục ngang CM.pdf tr.1
so_cuc | 2 | SUY RA: n ≈ 2900 /min ở 50 Hz = 2 cực
toc_do_vg_ph | 2900 | AQUARIS - Bơm trục ngang CM.pdf tr.2; PEROTAC - Bơm trục ngang CM.pdf tr.1; REDPUMP - Bơm trục ngang CM.pdf tr.1
dieu_kien | AQUARIS: temperatures not higher than 120 °C · Max. suction lift: 7 metres; PEROTAC: Liquid temperature between -10 °C and +120 °C · Ambient temperature between -10 °C and +50 °C · Max. working pressure 16 bar · Continuous duty S1; REDPUMP: Liquid temperature between -10 °C and +120 °C · Ambient temperature between -10 °C and +50 °C · Max. working pressure 16 bar · Continuous duty S1 | AQUARIS - Bơm trục ngang CM.pdf tr.1,2; PEROTAC - Bơm trục ngang CM.pdf tr.1; REDPUMP - Bơm trục ngang CM.pdf tr.1
dien_ap_3pha | 3~ 380–415 V | mọi catalogue CM: "3~ 380–415 V" ở trang 1
ghi_chu | CM: PDF chỉ có động cơ 3 pha; cột Q của bảng AQUARIS (0,6,9,12,15,18,21,24,27 m³/h…) khác PEROTAC/REDPUMP (0,6,9,15,18,24,27…) tùy trang: so sánh chỉ ở các Q trùng. Cột dong_A chỉ AQUARIS có (I tại 400 V). Ô '–' trong PDF = không có điểm, không đưa vào QH. | tự đối chiếu

## MODEL
hang | model_1pha | model_3pha | p2_kw | p2_hp | dong_A_1pha | dong_A_3pha | dien_ap_1pha | dien_ap_3pha | hong_hut | hong_xa | thong_so_khac | nguon | nghi_ngo
PEROTAC |  | CM 32-160/3 | 3 | 4 |  |  |  | 380–415 V | 50 | 32 |  | PEROTAC - Bơm trục ngang CM.pdf tr.2

## QH
hang | model | q_m3h | h_m | nguon
PEROTAC | CM 32-160/3 | 9 | 29.2 | BÁO GIÁ: 9–36 m³/h, 29.2–20.5 m (đầu dải); Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 12 | 28.8 | SUY RA: H = 29.7800 − 0.007160·Q² = 28.749, làm tròn 0,1 m → chọn 28.8 (làm tròn lên/xuống 0,1 m để đường mềm, lệch công thức ≤ 0,06 m); Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 15 | 28.2 | SUY RA: H = 29.7800 − 0.007160·Q² = 28.169, làm tròn 0,1 m; Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 18 | 27.5 | SUY RA: H = 29.7800 − 0.007160·Q² = 27.460, làm tròn 0,1 m; Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 21 | 26.6 | SUY RA: H = 29.7800 − 0.007160·Q² = 26.622, làm tròn 0,1 m; Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 24 | 25.6 | SUY RA: H = 29.7800 − 0.007160·Q² = 25.656, làm tròn 0,1 m → chọn 25.6 (làm tròn lên/xuống 0,1 m để đường mềm, lệch công thức ≤ 0,06 m); Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 27 | 24.5 | SUY RA: H = 29.7800 − 0.007160·Q² = 24.560, làm tròn 0,1 m → chọn 24.5 (làm tròn lên/xuống 0,1 m để đường mềm, lệch công thức ≤ 0,06 m); Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 30 | 23.3 | SUY RA: H = 29.7800 − 0.007160·Q² = 23.336, làm tròn 0,1 m; Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 33 | 22 | SUY RA: H = 29.7800 − 0.007160·Q² = 21.982, làm tròn 0,1 m; Báo giá BG-27102026-001 (27/10/2026) anh gửi
PEROTAC | CM 32-160/3 | 36 | 20.5 | BÁO GIÁ: 9–36 m³/h, 29.2–20.5 m (cuối dải); Báo giá BG-27102026-001 (27/10/2026) anh gửi